## Device to Symbol (built-in)
Device / meaning | Keyword pattern | LISA symbol
transformer (1PH/3PH resolved by phase); TX-x tag | \bXFMR¦TRANSFORMER\b¦\bTX-[A-Z0-9]¦\bTX\d | XFMR
VFD / soft-start / RVSS drive (VFD_L/_R block, now in library) | \bVFD¦\d+VFD¦VARIABLE FREQUENCY¦\bRVSS\b¦SOFT ?START | VFD
across-line / FVNR motor starter | \bMOTOR STARTER¦MTRSTRT¦\bFVNR\b¦STARTER\b | MTRStrt
pull section / pull box | \bUGPS\b¦PULL SECTION¦PULL ?BOX¦PULLBOX¦\bPB[X]?- | PullBox
a named control panel/cabinet is a terminal landing (TB), NOT a motor — even when 'PUMP' is in the name (e.g. PUMP CONTROL PANEL) | CONTROL PANEL¦CONTROL CABINET¦\bPCP\b¦\bLCP\b¦\bMCP\b¦\bRCP\b | TB_Square
motor / pump motor (1PH/3PH by phase) | \bMOTOR¦\bMTR\b¦\bMTR-¦\bPUMP\b¦\bPMP\b¦\bPMP- | MTR
flow meter / element | \bFLOW ?METER¦FLOWMETER¦MAG(NETIC)? ?FLOW¦\bFE-¦\bFE \d¦\bFM- | Inst
level element/sensor | \bLEVEL (TRANSMITTER¦ELEMENT¦SENSOR)¦\bLE-¦\bLE \d | Inst_Sensor
fused disconnect | FUSED DISCONNECT¦DISC.?FUSE | DISC_Fuse
disconnect | \bDISCONNECT\b¦\bDISC\b¦\bDISC- | DISC
circuit breaker | CIRCUIT BREAKER¦\bBREAKER\b¦\bCB-¦\bCB\b¦\bMCB\b | CB
fuse | \bFUSE\b¦\bFU- | Fuse
ground | \bGROUND\b¦\bGND\b¦\bEGC\b | GND
pressure switch (PSH/PSL/PSHL) | PRESSURE SWITCH¦\bPS[HL]L?\b¦\bPS- | PressureSwitch_NO
flow switch | FLOW SWITCH¦\bFSL\b¦\bFSH\b¦\bFS- | FlowSwitch_NO
level switch | LEVEL SWITCH¦\bLSL\b¦\bLSH\b¦\bLS- | LevelSwitch_NO
temperature switch | TEMP(ERATURE)? SWITCH¦\bTSL\b¦\bTSH\b¦\bTS- | TemperatureSwitch_NO
limit switch | LIMIT SWITCH¦\bZS-¦\bZSC\b¦\bZSO\b | LimitSwitch_NO
HOA/selector switch | \bHOA\b¦HAND.?OFF.?AUTO¦SELECTOR SWITCH | HOASwitch_NO
pushbutton | PUSH ?BUTTON¦\bPB-¦\bPBL\b | PushButton_NO
valve/solenoid | \bVALVE\b¦\bMOV-¦\bSOV-¦\bFCV-¦\bSV- | Valve
receptacle | RECEPTACLE¦RECEP¦\bGFI\b¦\bGFCI\b | RECP_Duplex
light/horn | LIGHT¦\bHORN\b¦BEACON¦STROBE¦ALARM HORN | LightHorn
heater | \bHEATER\b¦\bHTR\b | HTR
MTP fiber | \bMTP\b¦MULTI.?FIBER¦MTP- | MTP
LC fiber | \bLC\b(?!P) | LC
SC fiber | \bSC\b | SC
ST fiber | \bST\b | ST
ethernet/RJ45 | ETHERNET¦\bRJ45\b¦CAT ?[56]¦NETWORK SWITCH | RJ45
coax | \bCOAX\b¦COAXIAL | COAX
antenna | ANTENNA¦\bANT\b¦\bANT- | ANT
relay contact | \bCONTACT\b¦\bRELAY\b¦\bCR-¦\bICR\b | Contact_NO
pull/junction box | PULL ?BOX¦JUNCTION BOX¦\bJB\b¦\bJB- | PullBox
pull rope | PULL ?ROPE¦PULLROPE | Pullrope
spare | \bSPARE\b | Spare
analyzer/sensor (2/4-wire) | ANALYZER¦TRANSMITTER¦SENSOR¦\bAIT\b¦\bAE\b¦\bAE-¦\bAIT- | Inst_Sensor
instrument (2/4-wire) | \bFIT\b¦\bPIT\b¦\bLIT\b¦\bTIT\b¦\bFT-¦\bPT-¦\bLT-¦\bTT-¦INSTRUMENT | Inst
terminal block / panel | TERMINAL BLOCK¦\bTB-¦\bTB\b¦PANEL ?BOARD¦\bLCP\b¦\bMCC\b¦\bPLC\b¦\bPDP\b¦\bPBD\b¦\bCP-¦\bRIO\b¦\bLP-¦CABINET | TB_Square

## Device to Symbol (learned)
Device keyword | Symbol | Source / note
TERMINAL BLOCK | TB_Square | a terminal block symbol
CONTACT NO | Contact_NO | normally-open contact
GND | TB_Round | learned from a finished IDP drawing (73.1163-23E.dwg, block TB_Round_L)
PS-40-01 | PressureSwitch_NO | learned from a finished IDP drawing (73.1163-36E.dwg, block PressureSwitch_NO_R)
OPEN POSITION | TB_Square | learned from a finished IDP drawing (73.1128-80E.dwg, block TB_Square_L)
CLOSED POSITION | TB_Square | learned from a finished IDP drawing (73.1128-80E.dwg, block TB_Square_L)
CALL TO OPEN | TB_Square | learned from a finished IDP drawing (73.1128-80E.dwg, block TB_Square_L)
CALL TO CLOSE | TB_Square | learned from a finished IDP drawing (73.1128-80E.dwg, block TB_Square_L)
COMMON | TB_Square | learned from a finished IDP drawing (73.1128-80E.dwg, block TB_Square_L)
OPEN SIGNAL | TB_Square | learned from a finished IDP drawing (73.1128-80E.dwg, block TB_Square_L)
CLSOED SIGNAL | TB_Square | learned from a finished IDP drawing (73.1128-80E.dwg, block TB_Square_L)
REMOTE READY | TB_Square | learned from a finished IDP drawing (73.1128-80E.dwg, block TB_Square_L)
TB-AC1 | TB_Square | learned from a finished IDP drawing (73.1128-80E.dwg, block TB_Square_R)
TB-DC1 | TB_Square | learned from a finished IDP drawing (73.1128-80E.dwg, block TB_Square_R)
CALL TO STOP | TB_Square | learned from a finished IDP drawing (73.1128-80E.dwg, block TB_Square_L)
ACTUATOR 120V | TB_Square | learned from a finished IDP drawing (73.1128-80E.dwg, block TB_Square_L)
EXO202 PASS THROUGH | TB_Square | learned from a finished IDP drawing (73.1128-84E.dwg, block TB_Square_R)
OPEN STATUS | PullBox | learned from a finished IDP drawing (73.1128-85E.dwg, block PullBox_L)
CLOSED STATUS | PullBox | learned from a finished IDP drawing (73.1128-85E.dwg, block PullBox_L)
EXO302 PASS THROUGH | TB_Square | learned from a finished IDP drawing (73.1128-90E.dwg, block TB_Square_R)
CLOSED SIGNAL | TB_Square | learned from a finished IDP drawing (73.1128-17E.dwg, block TB_Square_L)
NEUTRAL | TB_Square | learned from a finished IDP drawing (73.1128-29E.dwg, block TB_Square_R)
VALVE OPEN | TB_Square | learned from a finished IDP drawing (73.1128-29E.dwg, block TB_Square_R)
VALVE CLOSED | TB_Square | learned from a finished IDP drawing (73.1128-29E.dwg, block TB_Square_R)
OPEN | TB_Square | learned from a finished IDP drawing (73.1128-29E.dwg, block TB_Square_R)
CLOSE | TB_Square | learned from a finished IDP drawing (73.1128-29E.dwg, block TB_Square_R)
L/R IN REMOTE | TB_Square | learned from a finished IDP drawing (73.1128-29E.dwg, block TB_Square_R)
PXOU34-1 PASS THROUGH | TB_Square | learned from a finished IDP drawing (73.1128-29E.dwg, block TB_Square_R)
PXOU34-2 PASS THROUGH | TB_Square | learned from a finished IDP drawing (73.1128-30E.dwg, block TB_Square_R)
PLC (DO) | TB_Square | learned from a finished IDP drawing (73.1128-31E.dwg, block TB_Square_L)
PLC (DI) | TB_Square | learned from a finished IDP drawing (73.1128-31E.dwg, block TB_Square_L)
PXO202 PASS THROUGH | TB_Square | learned from a finished IDP drawing (73.1128-38E.dwg, block TB_Square_R)
PXO302 PASS THROUGH | TB_Square | learned from a finished IDP drawing (73.1128-43E.dwg, block TB_Square_R)
TB-B | TB_Square | learned from a finished IDP drawing (73.1128-52E.dwg, block TB_Square_R)
RXO202 PASS THROUGH | TB_Square | learned from a finished IDP drawing (73.1128-52E.dwg, block TB_Square_R)
TB-C | TB_Square | learned from a finished IDP drawing (73.1128-53E.dwg, block TB_Square_R)
RXO302 PASS THROUGH | TB_Square | learned from a finished IDP drawing (73.1128-56E.dwg, block TB_Square_L)
FLS | FlowSwitch_NC | learned from a finished IDP drawing (73.1154-01E.dwg, block FlowSwitch_NC_L)
RJ45 | RJ45 | learned from a finished IDP drawing (73.1154-01E.dwg, block RJ45_L)
TAS | TemperatureSwitch_NC | learned from a finished IDP drawing (73.1154-01E.dwg, block TemperatureSwitch_NC_L)
VALVE | Valve | learned from a finished IDP drawing (73.1154-01E.dwg, block Valve_L)
EXO202 | PullBox | learned from a finished IDP drawing (73.1128-70E.dwg, block PullBox_R)
EXO302 | PullBox | learned from a finished IDP drawing (73.1128-71E.dwg, block PullBox_R)
VALVE ACTUATOR | PullBox | learned from a finished IDP drawing (73.1128-10E.dwg, block PullBox_R)
RXO202 | PullBox | learned from a finished IDP drawing (73.1128-55E.dwg, block PullBox_R)
RXO302 | PullBox | learned from a finished IDP drawing (73.1128-56E.dwg, block PullBox_R)
VALVE RXO302 | PullBox | learned from a finished IDP drawing (73.1128-62E.dwg, block PullBox_L)
PULL BOX | PullBox | learned from a finished IDP drawing (73.1154-03E.dwg, block PullBox_R)
ESW | RJ45 | harvested: ethernet switch (Stratford, PCWA)
3VFD | VFD | harvested: VFD bucket tag e.g. 3VFD1 (Crows) - boundary-safe
50-VFD | VFD | harvested: VFD tag 50-VFD-0x (Stratford)
MCS | MTRStrt | harvested: motor control section (Lake Supply)
MSS | MTRStrt | harvested: motor starter section (Lake Supply)
PDB | TB_Square | harvested: power distribution block (Lake Supply, Crows)
LANDING LUG | TB_Square | harvested: landing lug / neutral lug (Crows)
TB-DI | TB_Square | harvested: PLC discrete-input terminal (Stratford)
TB-AI | TB_Square | harvested: PLC analog-input terminal (Stratford)
TX- | XFMR | harvested: transformer tag TX-x (Stratford TX-LEQ, Crows TX-L)
OL- | MTRStrt | harvested: overload relay = motor-starter family (San Rafael OL-10/OL-20)
PANEL P2 |  | NEEDS REVIEW (L001, D side) — low-confidence match, fell back to CB-CB-CB-TB_Square_R. Set Result to the correct device token (e.g. CB, DISC, TB_Square, MTR).
WPPOWERJBOX @ FIT/FE 24-01 |  | NEEDS REVIEW (L003, D side) — low-confidence match, fell back to CB-TB_Square_R. Set Result to the correct device token (e.g. CB, DISC, TB_Square, MTR).

## Fill & Wire Conventions
Convention | Rule
Populate the SUPPORTING DOCUMENTS table (Ref Documents & Deviations) | Every conduit on a finished IDP cites the source drawings it was derived from, in the SUPPORTING DOCUMENTS block (DRAWING NUMBER / DESCRIPTION / MANUFACTURER). These live once, deduped, on the **Ref Documents & Deviations** sheet (A=index#, B=DWG#, C=Description, D=Manufacturer); each ConduitIndex row lists the matching index numbers in col J. Populate them, don't leave the template's prior-project refs (clear stale rows first). The set per conduit: (1) ALWAYS the design plans' conduit schedule / single-line the fill came from — DWG# = that sheet (e.g. `E-02`/`E-3`), MANUFACTURER = the owner/engineer of record (e.g. `STANISLAUS COUNTY`) read from the plan title block; (2) the AIC EDC drawing for the conduit's devices, BY TYPE — power feeder → `THREE-LINE DIAGRAM`, control/analog → `PLC I/O & CONTROL WIRING DIAGRAM`, panelboard branch → `PANELBOARD SCHEDULE` — with the real `73.xxxx-nn` number pulled from the EDC drawing index when it is in scope (e.g. 73.1188-05 THREE-LINE MSB1 & ATS1, 73.1188-91 MCC1); (3) any manufacturer CUT SHEET from the submittals that defines a device's terminals. Leave a DWG# blank + flag rather than fabricate a number. The extractor auto-applies (1)+(2)-by-type via `idp_terms.apply_supporting_docs`; pass `schedule_doc=(dwg,desc,manu)` for the real plan sheet, and fill EDC numbers from the index. [73.1188 Well2022 every sheet: E-02 STANISLAUS COUNTY + 73.1188-05 AIC three-line.]
Ground is classified by the S/D Tag = "GND", not the wire Type | LISA marks a conductor as GROUND in the conduit fill table ONLY when its S Tag or D Tag reads "GND" (workbook_mapper._derive_fill_slots → _tag_is_gnd); the GND_L/GND_R symbol and GRN color alone are NOT enough — without the tag LISA renders the green conductor as POWER and the GND block shows its default placeholder tag. So the ground conductor must carry **S Tag = D Tag = "GND"** with a BLANK terminal (GND is a tag, not a terminal number). Blanking the term also keeps the device-tag pass (CB-MAIN/CB-GEN, ATS N/E/L) from landing on the ground row. The extractor now does this for every ground — a separate GND group, a slot resolving to GND, or any GRN conductor (`idp_terms._is_ground_group` + `apply_source_info`). Verified through LISA's own parser: H001/H002/H005 now read 3×POWER + 1×GROUND.
Every real power feeder gets a ground — no false 'already grounded' | Verifying Crows 3 against LISA exposed feeders LEFT UNGROUNDED: (a) motor feeders to a `MTR_3PH_NoGND` block — the ground detector matched the substring 'GND' inside 'NoGND' and thought a ground already existed (fixed: strip NO[_ ]GND, then match GND as a token); (b) panel feeders that already carry EDC/panelboard circuit terminals — the source-info pass skipped them, so the ground group's tag never became 'GND'. The writer now forces S Tag = D Tag = 'GND' (blank term) on EVERY ground group unconditionally. Result on 73.1188: 34/34 POWER feeders grounded, 0 missing. Pull-rope / fiber / empty conduits still correctly get NO ground.
PLC I/O channels are the control/analog terminations | The MASTER-PLC-side term on a control/analog cable is its PLC I/O channel, read from the Main PLC EDC I/O sheets by matching the field device to a point: a discrete status/interlock → a DIGITAL INPUT channel on `TBDI-0.<slot>` (e.g. smoke → `TBDI-0.02:15`, door → `TBDI-0.03:00`); an analog transmitter → an ANALOG INPUT channel on `TBAI-0.<slot>` (e.g. tank level `LT` → `TBAI-0.08:01`, VFD speed → `TBAI-0.07:02`, TSS/pH → `TBAI-0.07:00/01`); a PLC→field command → a DIGITAL OUTPUT on `TBDO-0.<slot>`. The term lands on whichever conduit END is the MASTER PLC. Label reads `MASTER PLC:TBAI-0.07:02/DEVICE:…`. Slots/channels come from the EDC PLC I/O drawings (56.1059-05/-06 DI, -10/-11 AI); match by device, never fabricate a channel. [Moccasin 56.1059 Main PLC EDC]
kcmil sizes are MCM, not AWG | Large conductors sized in kcmil (a bare number >=250, e.g. 350/500/750 — often written just as `4CC-350` on a cable schedule) are a DIFFERENT sizing system than AWG. Render them as `NNN MCM`, never `#350AWG`. The extractor normalizes bare kcmil gauges to `NNN MCM` (`idp_anatomy.apply_conventions`) and LISA's `_with_awg` skips the AWG suffix when the size contains MCM/KCMIL. AWG (#10, #4/0) keeps its `#`. [Moccasin 56.1059 C-001 4CC-350 → 350 MCM]
Panelboard voltage decides 1Ø vs 3Ø — read the schedule | Don't assume a 3-conductor branch is 3-phase. A 120/240V 1Ø panelboard's branches are L/N/G (BLK/WHT/GRN), landing on ONE circuit (`PANEL-4:CKT-9/load:L`, `PANEL-4:N/load:N`); a 480V 3Ø panel's feeders are ØA/ØB/ØC(+N)+GND on a 3-pole breaker. Read the PANELBOARD SCHEDULE's VOLTAGE/PHASE header + the circuit→load map to set the panel-side S Tag = the panel and S Term = the circuit number (1Ø) or phases (3Ø). AUTOMATIC APPROXIMATION (no schedule/vision): the extractor now infers 1Ø from the ground pattern — a 2–3-wire POWER group carrying its ground INTEGRALLY (no separate 'W/GND' EGC group, branch gauge) is single-phase → BLK/WHT/GRN + L1/N/G; a group with a SEPARATE green EGC is 3Ø → ØA/ØB/ØC + GRN (`idp_anatomy._is_single_phase_branch`). The exact circuit number still needs the schedule/vision. [Moccasin PANEL-4 = 120/240V 1Ø #56.1059-11; PANEL-3 = 480V 3Ø #56.1059-10]
EDC supporting docs are selected by FILL TYPE, any tag scheme | The AIC EDC drawing cited per conduit follows its circuit type, regardless of the conduit-tag naming (P/C/A, K-###, …): POWER feeder → THREE-LINE, POWER branch (panel circuits) → PANELBOARD SCHEDULE, CONTROL → PLC I/O DIGITAL, TSP → PLC I/O ANALOG, CAT-6 → NETWORK LAYOUT, FIBER → FIBER OPTIC LAYOUT — plus the SFPUC/owner design sheets (one-line, conduit & cable schedules) on every conduit. `idp_terms.apply_supporting_docs` now keys off the fill types (not the tag prefix). Author = the EDC firm (e.g. W. M. LYLES); real `56.1059-##` numbers come from the EDC index.
Wire labels follow the FILLWIRELABEL tool grammar, written as a LITERAL | Each conductor's Wire Label is the terminal cross-reference the AutoCAD FILLWIRELABEL tool builds: **SrcName:SrcTAG1:SrcTerm / DstName:DstTAG1:DstTerm** (e.g. "NEW T.I.D. XFMER:XFMR:ØA/UGPS:ØA", "CHUNGUS:GFR:21/CHUDCENTRAL:TBDI-0.01:CBD6"). Rules mirrored from the LISP: the MIDDLE field is the device block's TAG1 (its baked device designator — XFMR/CB/MTR/DISC/GND from the symbol library device_default; `idp_terms.device_tag_for_symbol`), shown on EVERY conductor; the NAME is dropped when it equals the tag; blank fields collapse (join non-empty with ":"). Names come from Src_Name01/Dst_Name01. The template stores this as a TEXTJOIN formula, but openpyxl can't evaluate formulas so the cached value was blank and LISA (data_only) fell back to printing the wire TYPE ("POWER"). The extractor now writes the computed LITERAL to Wire Label 1-4 (idp_write) and fills a blank S/D Tag with the symbol's device tag so both the block AND the label carry it. Hand-built FillIndexes must write literal labels, not un-recalculated formulas.
Utility service lateral carries NO separate ground (EGC) | A utility service lateral — a utility transformer (T.I.D / SMUD / PG&E / TURLOCK / "UTILITY") feeding the service point (UGPS / MSB / switchboard / meter) — has NO equipment ground conductor in the raceway; grounding is done at the service via the grounding-electrode conductor. Finished IDP H2201 (T.I.D XFMER → MSB1) draws it as 3×500 MCM phases, no ground. `ensure_ground` now skips these (idp_anatomy._is_utility_service) while still grounding every real feeder/motor/panel branch. This is the ONE case where a POWER feeder legitimately has no ground.
MCM/KCMIL sizes get a stray "AWG" suffix (LISA-side note) | LISA's workbook_mapper._with_awg appends "AWG" to any size whose core starts with a digit, so a 750 MCM aluminum conductor renders as "#750 MCM ALAWG". MCM/KCMIL and AWG are different sizing systems — AWG should not be appended to an MCM size. This is a LISA rendering issue (the extractor writes the correct "750 MCM AL"); the fix is one guard in _with_awg to skip when the value contains MCM/KCMIL.
SUPPORTING DOCUMENTS sheet must be named "Ref Documents" | LISA finds the supporting-docs / deviation-notes sheet ONLY by the exact name "Ref Documents" (or "Ref Docs"); the template's "Ref Documents & Deviations" is invisible to it, so the table renders blank no matter how it's filled. The extractor renames the sheet to "Ref Documents" in the output workbook (template untouched). When building the FillIndex by hand, put the ref docs on a sheet named exactly that.
ATS terminals by connection role (N/E/L) | An Automatic Transfer Switch labels its phase terminals by ROLE: Normal `NA/NB/NC/NN` (from the utility/MSB source), Emergency `EA/EB/EC/EN` (to/from the generator), Load `LA/LB/LC/LN` (to the downstream MCC/panel). Only the ATS end is prefixed; the other end keeps its phases. [73.1188 H2202 dest=NA…, H2203 src=EA…, H2204 src=LA…]. The extractor auto-applies this (`idp_terms.apply_power_terminals`) — the device-specific power terminal the EDC three-line carries.
Pull device data from submittals when needed | When the conduit schedule / EDC leaves a value blank, mine the project SUBMITTALS: vendor CUT SHEETS give a device's terminal names/count, model, and ratings (e.g. a transmitter's loop terminals, a starter's OL/aux contacts); the `…_SCL_` Submittal Cover Letter gives project conventions and deviations (conduit material, wire-color changes, removed/added conduits); vendor quote/BOM docs confirm make/model. Match a cut sheet to a device once and apply it across every IO point that shares that make/model (flag the spread). Never fabricate — if the submittal doesn't state it, leave blank and flag.
Clean input beats OCR — and normalize OCR text | The skill/clean path reads structured text so it has no punctuation noise; the exe OCR path picks up spacing/dash noise (`MCC1-SEC.2` vs `MCC1-SEC. 2`, em-dash `ZS-01—A`, `@EYE`). That noise — not logic — is most of the skill-vs-exe accuracy gap on a vector schedule. The OCR reader now normalizes it (dash→hyphen, letter-period-digit spacing, `@` spacing) WITHOUT touching unit names or decimals (`idp_ocr_schedule._normalize_text`). For true skill-level accuracy on a vector sheet, feed the conduit schedule as an Excel/clean source (the bridge) rather than relying on OCR; OCR is the ~95% fallback with amber-flagged cells.
Control panel is a landing, not a motor | A named CONTROL PANEL / CABINET / PCP / LCP / MCP is a terminal-block landing (`TB_Square`), even when the name contains PUMP (e.g. `PUMP CONTROL PANEL`). Only a real motor/pump LOAD (`WELL PUMP P-01`, `MTR`, `PMP-`) is `MTR_3PH`. Enforced in `symbol_infer` ahead of the motor rule.
Meter/Main & service are upstream | For Source↔Dest orientation, a METER/MAIN, metered PEDESTAL, service entrance or PDB is UPSTREAM (source) of panels, PCPs and loads — rank it just below the utility. Fixes feeders like Meter/Main→PCP reading backwards. (`idp_anatomy._elec_rank`)
VFD block (VFD_L/_R) now exists — use it for VFD/RVSS | A `VFD`/`RVSS`/soft-start/`nVFDn` bucket feeding a motor now maps to the **`VFD_L/_R`** block (authored from MTRStrt: POWER, 3 terminals, Tag1='VFD'; registered in the cascade, contract, BlockIndex, and library DWGs). An across-line / FVNR starter still uses `MTRStrt`. So distinguish: drive → `VFD`, contactor+OL → `MTRStrt`. [Crows 3VFD1 → VFD_L]
Symbol-library terminal capacity is known | Each library block's terminal capacity is cataloged from its DWG (Term1..n attribute defs): 1-term ×36, 2-term ×63, 3-term ×44, 4-term ×26, 0-term ×6. A symbol may only carry a wire group whose Wire Ct ≤ its terminal capacity — see `symbol_library_catalog.json` / the 'Symbol Library (DWG)' sheet in Learned Logic.xlsx.
Source/Dest info on EVERY row | Populate the SOURCE and DEST side of every fill row, not just grounds: the **S/D Symbol** = the device block for that end (`symbol_infer`); the **S/D Description** = the equipment name from the ConduitIndex Source/Dest (e.g. `MCC1-SEC. 2`, `1200A MSB`, `PANEL L`) on EVERY group; the **S/D Term** = the terminal landing — phases `ØA/ØB/ØC`(+`N`) on power feeders, `GND` on the separate ground conductor, breaker/circuit numbers on panelboard branches, and the EDC channel/loop terminals on signal/control. EDC-provided terminals win; convention fills the rest. The extractor auto-applies this (`idp_terms.apply_source_info` + `apply_panelboard_circuits`); a finished IDP never leaves a source blank.
Ground gauge from the schedule | When the conduit/cable schedule lists a ground size (its GND column, e.g. `#2/o`, `#6`, `#8`), the `GRN` ground row uses THAT gauge — never a fabricated default. A schedule that lists grounds is authoritative: a conduit with none listed (utility service) gets NO ground. Motor blocks stay `MTR_3PH_NoGND` because the ground is its own row. (`idp_excel`/`idp_schedule` carry the gauge; `idp_anatomy.ensure_ground` only synthesizes where the schedule is silent about grounds.)
Cable color | PULL_ROPE / FIBER / CAT-6 carry no wire color → set Color to `N/A` (never blank, `XXX`, or a descriptor like `ETHERNET`). [Stratford1: P001, C003, C010–C013, C020A/B]
Analog signal type | A field-instrument analog signal pair (transmitters / level / flow / pressure — e.g. EFFLUENT FLOW, EFFLUENT PRESSURE, tank LEVEL) is ONE `TSP` with color `RED/BLK`, NOT two discrete `CONTROL` wires. [Stratford1: C004, C005, C008, C009, C017] — the extractor auto-applies this (`idp_anatomy.merge_analog_pairs`); you should too.
Ground on control/signal conduits | Every real-circuit conduit carries a ground conductor shown `GRN`. In the current template it is a separate `POWER` / Wire-Ct-1 / `GND` / `GRN` fill (the only legal way to carry the GND symbol; the older sets used a `GROUND` type not in the current dropdown). [Stratford1: C002, C006, C010–C013, C015, C018] — the extractor auto-applies this (`idp_anatomy.ensure_ground`); you should too.
Power phase colors | 3-phase POWER = `BRN / ORG / YEL` (+ `WHT` neutral when 4-wire) + `GRN` ground — confirmed against LISA output (H002, H005).
Discrete switch vs. analog transmitter | A field **switch** (pressure/level/flow switch — `PSH`/`PSL`/`LSH`/`FSH`/`TSH`/`ZS`, or the word SWITCH) is a DISCRETE dry contact → `CONTROL` wiring, NOT a `TSP`, even though its name contains PRESSURE/LEVEL/FLOW. Only a **transmitter** (`PIT`/`LIT`/`FIT`/…`IT` or the word TRANSMITTER) is analog → `TSP` `RED/BLK`. [Lennar C061 DISCHARGE PRESSURE SWITCH = 2× CONTROL `BLU`; A071 FLOWMETER = TSP; A051 LEVEL TRANSMITTER = POWER+TSP] — now enforced in `idp_anatomy.merge_analog_pairs`.
Loop-powered analog instrument | A 2-wire loop-powered transmitter (e.g. a level transmitter `LIT`) lands loop `POWER` (2 conductors) PLUS the `TSP` signal pair — not TSP alone. [Lennar A051: POWER `#14` `BLU`/`BLK` + TSP `#18` `RED/BLK`]
Utility service entrance | The utility-transformer→meter/main service conduit is `POWER` with fill size/color **per utility** (leave the drawing's `TBD` and flag it — do not invent a gauge/color); it carries `ØA/ØB/ØC/N` and takes NO separate equipment ground (utility secondary). [Lennar P001]
Blocks from the device, terms from the wiring diagram | The **S/D Symbol** (block) is inferred from the DEVICE at each end (`symbol_infer`): transformer→`XFMR_3PH` (incl. a `TX-x` tag), **motor OR pump** (`MOTOR`/`MTR`/`PUMP`/`PMP`/`PMP-`)→`MTR_3PH` on a 3-conductor feeder (phase resolved by Wire Ct, not just the name), pressure/level/flow **switch** (`PSH`/`PSL`/`PSHL`/…)→`PressureSwitch`/`LevelSwitch`/`FlowSwitch`, disconnect→`DISC`, a panel / MCC / MSB / ATS / PLC / enclosure → `TB_Square` (terminal block, the default landing), ground→`GND`, pull rope→`Pullrope`, ethernet→`RJ45`. Do NOT leave everything as generic CB/TB — recognize the real device so the symbol matches the finished IDP. The **S/D Term** (terminal landing) is NOT on the conduit/cable schedule — read it from the AIC EDC three-line / terminal / wiring diagrams. **Do not change the workbook's own fill logic (types, counts, colors) and NEVER relabel the phases: power conductors stay `ØA/ØB/ØC` (+`N`) on BOTH ends** — the S/D Tag carries the EDC equipment (e.g. `MSB1`, `ATS1`, `EG1`), the term stays the phase. [Crows Landing 73.1188 DWG 73.1188-05: H005 `EG1:ØA/ØB/ØC/N → ATS1:ØA/ØB/ØC/N`; H003 `MSB1 → ATS1`, phases ØA/ØB/ØC]. The conduit/cable schedule (plans) owns the ConduitIndex; only terms/tags/blocks adhere to the EDC — the fill logic is unchanged.
Source block from BOTH ends; simple real blocks not generic CB/TB | Pick the block from the device at that end AND the other end — an MCC/VFD/RVSS bucket feeding a **motor/pump** is a **motor STARTER** (`MTRStrt`), not a plain breaker; a conduit fed **from a transformer** (`TX-x`) shows `XFMR_3PH` on the source; a **pull section / UGPS / pull box** is `PullBox`; a switchboard main is breakers (`CB`). Only fall back to the generic terminal-block/breaker block when the device is genuinely unknown — don't leave everything CB/TB. (`idp_anatomy.refine_source_symbols` does this from the src+dest pair.)
Tags vs. descriptions | The **S/D Tag** columns are for a real device/terminal tag (e.g. an ISA point `YA-10`) — NOT the equipment name. The equipment NAME/description (e.g. `PANEL L`, `MCC1-SEC. 2`, `UGPS`) goes in the **S/D Description** columns; the wire label already pulls the name from the ConduitIndex Source/Dest Name. Leave the Tag blank when there's no sub-tag.
Where each terminal comes from (term source map) | Read `S/D Term` from the matching EDC sheet by circuit kind: **3-phase power feeders** → the three-line (terms = phases `ØA/ØB/ØC`(+`N`/`GND`), tag = equipment); **120/208V branch circuits** → the **PANELBOARD SCHEDULE** (S Tag = the panel, e.g. `PANEL L`; S Term = the breaker/circuit numbers from the `L1-2,4,6`-style note; S Rating = the breaker amps) — and cross-check the circuit's panelboard description against the conduit's destination to catch a wrong circuit ref; **discrete control** (status/interlocks) → the **PLC DI sheets** (D Term = the PLC channel address `0.2.dd.dd`, tag = the ISA point, e.g. generator `YA/YH/YR/YF-10` → `0.2.01.05-08`); **analog instruments** (flow/level/pressure transmitters) → the **analog-input (AI) sheets** (term = the AI channel `0.2.0x.xx` and subpanel `TB` pair, tag = the loop, e.g. `FIT P-04`→`FOP-04`@`0.2.06.06`, `LIT-4001`@`0.2.05.01`). A pump **PSHL** pressure switch is usually a hardwired VFD protection interlock on the pump ELEMENTARY sheet (VFD terminals), not a PLC point. [Crows Landing 73.1188 DWG -05/-51/-54/-65/-69/-70/-71 + Panel L panelboard schedule]
Extract EDC terminal landings — what generation needs, and how each is read | Generation needs the S/D TERM (the landing) on every conduit, and it comes from the AIC EDC submittal by circuit kind — NOT from the plans: **3-phase feeders** → the three-line, terms = phases ØA/ØB/ØC(+N/GND); **120/240V branches** → the PANELBOARD SCHEDULE, panel-side term = the circuit CKT-## (tag = the panel); **discrete control** → the PLC DIGITAL-INPUT/OUTPUT block (term tag = TBDI-0.0n / TBDO-0.0n); **analog instruments** → the PLC ANALOG block (term tag = TBAI-0.0n). How the extractor reads them, in order: (1) TEXT-LAYER channel addresses (`0.r.ss.cc`) when the EDC exports them as text (`idp_edc.parse_io_sheets`); (2) OFFLINE POSITIONAL read of AIC LADDER sheets — the common form — where the channel NUMBER is graphical but the device DESCRIPTIONS are real text and channels run sequentially (INPUT 00,01,…): read the description blocks in the sheet's READING order (via the page rotation matrix — these sheets are rotated 270°), keep SPARE rungs + disambiguating digits (VFD 1 vs 2), drop the TB-tag/module/title blocks, and the POSITION IS the channel → exact TB:channel with NO OCR and NO vision, in ~0.5s (`idp_edc.parse_io_positional`/`match_io_positional`, hard-filtered analog↔digital). (2b) TB-only ladder fallback flags `edc_io_tb=…(verify channel#)` for anything the positional read can't resolve; (3) PANELBOARD by LOAD — derive CKT-## by matching the conduit's load name to the schedule's circuit descriptions when the note has no explicit circuit (`idp_terms._match_load_to_ckts`, flag `panelboard_circuits_by_load(verify ckt#)`); (4) VISION ESCALATION — when the EDC sheet is pure vector (channel/CKT numbers are geometric on rotated ladder drawings, so NOT reliably text-readable), render the sheet and transcribe via API key or the ASK_CLAUDE_EDC.md packet to get exact channels. Never fabricate a channel/circuit number — land the TB/panel tag and flag the number for a quick check. Feed the EDC PDFs to the run (`apply_edc_terms_from_paths`); without them the terms stay blank. GOTCHA: when a CABLES-IN-CONDUIT list is folded into a conduit's note, do NOT read its cable IDs as panelboard circuits — `C-021` is cable 21, not circuit 21. Strip the cable list before parsing circuit numbers (`idp_terms._strip_cable_list`); otherwise a panel branch lands on a bogus circuit and blocks its real phase terms. [56.1059 Main PLC: TBDI-0.02/0.03, TBAI-0.07/0.08 matched by device; channels via vision. 73.1188: text-layer channel addresses parsed directly.]
Fill precision needs the CABLE schedule — the conduit schedule alone under-specifies | The conduit schedule (MC-E-8 / E-3) lists WHICH cables run in eachconduit and a coarse TYP (POWER/CONTROL), but NOT the per-conductor specs. The conductor count, gauge, insulation/type (TSP vs CAT-6 vs FIBER vs a mfg cable), and — critically — whether a run carries a green EGC all live on the **cable schedule** (MC-E-9 / the C-### cable list). Comparing the Moccasin 56.1059 auto-run (conduit schedule only) against the curated fill made the gap concrete: (a) **over-grounding** — with no ground column, the writer synthesized a ground on every circuit (61 grounds vs the 25 the cable schedule actually lists), so control/signal/spare runs got a false EGC; (b) **coarse types** — everything collapsed to POWER/CONTROL, losing the real TSP/CAT-6/FIBER/MFG_CABLE distinctions. So: derive fill from the CABLE schedule when one exists; the conduit-schedule TYP is only a fallback seed. When you must run conduit-schedule-only, mark the records NOT ground-authoritative and flag the synthesized grounds + coarse types (`ocr_conduit_only_fill_from_cables`) so the confidence score reflects the assumption rather than reading as complete. [56.1059 skill-v9 curated=25 grounds/precise types vs exe-v1 auto=61 grounds/POWER-CONTROL only]

## Conduit Conventions
Convention | Rule
A finished AIC IDP is ONE CONDUIT PER SHEET — read it by OCR, not the text layer | An AIC interconnection-diagram finished IDP (title 'INTERCONNECTION DIAGRAMS') draws one conduit per sheet, and the identity + fill are GRAPHICAL (the PDF text layer carries almost none of it — the text-only reader recovers ~7 of 24). Read each sheet by OFFLINE OCR instead (idp_idp_ocr.read_interconnection_idp): the FIELD header gives `NAME: <tag>` (the conduit), `TYPE: <PVC/RGS/…>`, `SIZE: <4"/2"/3-4">`; the SOURCE label (top-left) and DESTINATION label (top-right) give from/to; and the FILL TYPE table (FILL TYPE ¦ SIZE ¦ COLOR ¦ QUANTITY) gives the conductors. Fill vocabulary → LISA type: POWER→POWER, CONTROL→CONTROL, GROUND→ground group (S/D Tag GND), TSP→TSP (RED/BLK), PULL ROPE→PULL_ROPE, ETHERNET→CAT-6, fiber (OM3/SMFO)→FIBER, NONE→empty conduit. QUANTITY is the conductor count; SIZE like `#10AWG`/`400KCMIL`/`#18` is the gauge; a `XXX`/`XX` NAME/TYPE/SIZE means the sheet itself flags it TBD (don't invent). Learned from City of Gonzales Industrial WWTF (56.1113): 24 conduits offline vs 7 by text.
Conduit tags can be ANY scheme — circuit class lives in the TYP column | Don't assume AIC's P/C/A prefix. Some owners tag every conduit with one prefix (e.g. Moccasin 56.1059 uses `K-001…K-067` for power, control, and ground alike) and put the circuit class in a separate TYP column (POWER / CONTROL / GROUND / PWR-CONTRL). Take `conduit_name` verbatim from the schedule; read the class from TYP (or the fill), never from the tag prefix.
SIZE column often combines trade size + material | A conduit-schedule SIZE cell like `2" PVC`, `1.25" RGS`, `3/4" RGS` carries BOTH the trade size and the material. Split it: `conduit_size` = the trade size (`2"`), `conduit_type` = the material normalized to the enum (PVC / RGS). A COMMENT of "EXPOSED/SURFACE MOUNT TO BE RGS" means the run is PVC buried but RGS where exposed — keep the design material as `conduit_type` and note the RGS-exposed nuance. [Moccasin MC-E-8]
Generator stays the destination (keep schedule direction) | A generator (`EG#`, ENGINE GENERATOR) connected to an ATS is drawn by AIC as the DESTINATION, not the source — the finished IDP keeps the conduit schedule's FROM/TO (`ATS→EG1`), NOT the electrical direction. [73.1188 H2203: SOURCE=ATS1, DEST=EG1]. Do not flip a generator conduit to make the generator upstream. (`idp_anatomy._elec_rank` ranks EG as a load on every conduit.)
Index-less IDP packages | Some finished IDP PDFs have NO drawing-index page and interleave client spec pages with the diagrams (e.g. San Rafael 56.1125, conduits named S1/E05). The reader enumerates conduits directly off each diagram page — anchoring the conduit id to the NAME: label (rotation-agnostic) with a broadened id pattern (`[A-Z]{1,3}\d{1,4}`). Such packages parse only partially (non-standard layout/geometry) — verify the conduit count and flag gaps rather than assume completeness. (`idp_idp_pdf._parse_page_fills`)
Only real, documented conduits | Emit one ConduitIndex row per physically documented run — no speculative or duplicated conduits. Training on finished sets showed over-production (Stratford: ~72 emitted vs ~42 real). If a run isn't in the schedule or schematic, flag it — never invent it.
Conduit Type normalization | Normalize the source MATERIAL / TYPE to the `Conduit Type` enum: `PVC-40` / `PVC-80` → `PVC`; `GRC` / rigid galvanized → `RGS`; `RMC` stays `RMC`. An unknown/absent type → `XXX` + a flag, never blank and never a guessed material.
Wire fill stays out of ConduitIndex | A conductor / wire-fill column in the schedule is Phase 1b (FillIndex) input, not a conduit field. Retain the text separately for FillIndex and note anything unusual in `deviations_notes`.
Target fast + remember layouts — don't deep-scan every file | On a big project folder, don't OCR/full-scan every file. TARGET like the skill does: skip irrelevant subtrees by folder (estimating, quotes-received, photos, correspondence, PMO) and extension without opening them; decide cover letters (`_SCL_`/`_CL_`/transmittal) and vendor cut sheets (datasheet/catalog, or a Cut-Sheets folder) by NAME/FOLDER — vendor datasheets resemble PLC-I/O content, so never classify them by content. Recognize a document by its LAYOUT SIGNATURE from the first page (`idp_layouts`: seed token sets per role + tokens LEARNED from confirmed examples, confidence gated on the SEED overlap so one over-fit example can't mislabel a related doc). Only relevant files whose type isn't recognized by signature fall through to the authoritative full-document finders — and each confirmed type is LEARNED so the next project is faster. [56.1059: skipped Estimating/Quotes; Eaton Dwg_Panel→panelboard, moxa datasheet→cut_sheet by name, EDC PLC→edc_plc_io.]
Route a whole project folder — each field knows its source | Given an entire project folder, classify EVERY file by ROLE and populate each workbook field from the source that actually carries it, instead of hand-picking files (`idp_router.classify`). Roles: CONDUIT SCHEDULE (conduit name/src/dst/size/type), CABLE SCHEDULE (fill type/gauge/colors + grounds), EDC THREE-LINE (3Ø feeder phase terms), PANELBOARD SCHEDULE (branch CKT-##), EDC PLC I/O (TBDI/TBAI control+analog terms), CUT SHEETS + project DWGs (S/D symbols), finished IDP (reference / conduit source of LAST resort only), cover letters + cut sheets (NO conduit data — kept out of conduit extraction). Detect by the authoritative full-document finders (find_schedule_pages / find_cable_schedule_pages / find_edc_sheets / is_idp_package), NOT just head-text — a conduit schedule can sit on page 37 of a 55-page plan set. Pick the LATEST revision per single-source role (R##/date in the filename). Log the field→source map so it's auditable. [56.1059: Plans→conduit_schedule, EDC Main PLC→edc_plc_io, Eaton Dwg_Panel→panelboard, *_SCL_*→cover_letter, datasheet→cut_sheet]
Hand FillIndex the CABLE schedule, not just the conduit schedule | When a project splits its schedules — a **conduit schedule** (MC-E-8: id / TYP / FROM / TO / SIZE / cables-in-conduit) and a separate **cable schedule** (MC-E-9: C-### / SIZE / TYPE-INSUL / FROM / TO / which conduits it routes through) — capture BOTH and pass the cable schedule through for Phase 1b. The conduit schedule alone lets FillIndex seed only a coarse POWER/CONTROL fill and forces it to synthesize grounds blindly; the cable schedule is what carries the per-conductor gauge, insulation/type, and green-EGC presence. Note the cable-schedule sheet id in the conduit record so FillIndex knows where the real fill data is. [Moccasin 56.1059 MC-E-8 conduit + MC-E-9 cable]
Prefer the finished IDP package as source | When a project has AIC's own finished IDP submittal PDF (`…_Prj_IDP_<date>.pdf` — a drawing-index page + one interconnection-diagram page per conduit), extract from THAT, not the marked-up contract plans, which are usually scanned/vector with no text-extractable schedule. [Lennar: `Plans (Marked-Up).pdf` → nothing; the finished IDP → all 7 conduits] The extractor auto-detects this format (`idp_idp_pdf`).
`_SCL_` is a Submittal Cover Letter, not a schedule | A `…_IDP_SCL_<date>.pdf` is the cover letter / review-comments log — do NOT parse it for conduits. Mine it for project conventions and RFI/deviation responses (conduit material, wire color changes, removed conduits). [Lennar SCL: all conduits PVC SCH40; C061 control changed to BLU; spares X001–X003 removed]
Conduit-tag prefix hints at circuit class | AIC tags `P###` = power feeders, `C###` = control, `A###` = analog/instrument. Use as a weak type hint — always confirm against the actual fill, never as the sole basis.
Source/Destination follow electrical direction | Orient each conduit so **Source = the upstream end** (where power/signal originates) and **Destination = the downstream end** (the load / field device), per the distribution hierarchy: utility → transformer → UGPS → MSB → ATS → MCC → panel → VFD/starter → motor/load; PLC/controller is the source for a control conduit. A schedule's FROM/TO may be listed backwards — fix it. Dual-role gotcha: a **generator** is the SOURCE on its main feeder (it feeds the ATS, so `ATS→EG` becomes `EG→ATS`) but the DESTINATION for its auxiliaries (block heater / charger / controls, fed by an MCC or panel); disambiguate by the fill — a main feeder uses MCM/large conductors. [Crows Landing 73.1188: H005 corrected to EG1→ATS] — enforced by `idp_anatomy.orient_by_electrical_direction`.

## OCR & Accuracy Logic
Logic | What it does | Where
Vector schedule OCR | Locate table upper-left, render ~500 DPI, OCR, bin to columns. Offline. | idp_ocr_schedule
High-accuracy 2-pass | Re-crop tight + re-OCR 560 DPI. ~86%->95%. | read_schedule refine
ID sequence repair | Implausible conduit # snaps to running sequence. | _repair_ids
Name self-consistency | Rare name misread snaps to frequent canonical; guards distinguishing digits. | _repair_names
Prime/quote normalize | Curly quotes/primes unified (vault names). | read_schedule
MSB boundary | 1000AMSB -> CB-CB-CB not TB. | refine_source_symbols
Notes column | Notes -> panel circuit numbers. | idp_excel/idp_schedule
Source info every row | Symbol+Term+Description on every group, not just grounds. | apply_source_info
Ground from schedule | Real GND gauge; authoritative (utility gets none). | ensure_ground

## Symbol Library (DWG)
Block | Device tag | Terminals | Tag slots | Geometry
ANT_L | ANT | 1 | 1 | Line:5
ANT_R | ANT | 1 | 1 | Line:5
CB-CB-CB-TB_Round_L | CB | 4 | 4 | Arc:3, Circle:7, Line:5
CB-CB-CB-TB_Round_R | CB | 4 | 4 | Arc:3, Circle:7, Line:5
CB-CB-CB-TB_Square_L | CB | 4 | 4 | Arc:3, Circle:6, Line:5, Polyline:1
CB-CB-CB-TB_Square_R | CB | 4 | 4 | Arc:3, Circle:6, Line:5, Polyline:1
CB-CB-CB_L | CB | 3 | 3 | Arc:3, Circle:6, Line:6
CB-CB-CB_R | CB | 3 | 3 | Arc:3, Circle:6, Line:5
CB-CB-TB_Round_L | CB | 3 | 3 | Arc:2, Circle:5, Line:3
CB-CB-TB_Round_R | CB | 3 | 3 | Arc:2, Circle:5, Line:3
CB-CB-TB_Square_L | CB | 3 | 3 | Arc:2, Circle:4, Line:3, Polyline:1
CB-CB-TB_Square_R | CB | 3 | 3 | Arc:2, Circle:4, Line:3, Polyline:1
CB-CB_L | CB | 2 | 2 | Arc:2, Circle:4, Line:3
CB-CB_R | CB | 2 | 2 | Arc:2, Circle:4, Line:3
CB-TB_Round_L | CB | 2 | 2 | Arc:1, Circle:3, Line:1
CB-TB_Round_R | CB | 2 | 2 | Arc:1, Circle:3, Line:1
CB-TB_Square-TB_Round_L | CB | 3 | 3 | Arc:1, Circle:3, Line:1, Polyline:1
CB-TB_Square-TB_Round_R | CB | 3 | 3 | Arc:1, Circle:3, Line:1, Polyline:1
CB-TB_Square_L | CB | 2 | 2 | Arc:1, Circle:2, Line:1, Polyline:1
CB-TB_Square_R | CB | 2 | 2 | Arc:1, Circle:2, Line:1, Polyline:1
CB_L | CB | 1 | 1 | Arc:1, Circle:2, Line:1
CB_R | CB | 1 | 1 | Arc:1, Circle:2, Line:1
COAX_L | COAX | 1 | 1 | Circle:4
COAX_R | COAX | 1 | 1 | Circle:4
Contact_NC_L |  | 2 | 1 | Line:6
Contact_NC_R |  | 2 | 1 | Line:6
Contact_NO_L |  | 2 | 1 | Line:5
Contact_NO_R |  | 2 | 1 | Line:5
DISC-DISC-DISC-TB_Round_L | DISC | 4 | 4 | Circle:7, Line:11
DISC-DISC-DISC-TB_Round_R | DISC | 4 | 4 | Circle:7, Line:11
DISC-DISC-DISC-TB_Square_L | DISC | 4 | 4 | Circle:6, Line:15
DISC-DISC-DISC-TB_Square_R | DISC | 4 | 4 | Circle:6, Line:11, Polyline:1
DISC-DISC-DISC_Fuse-TB_Round_L | DISC | 4 | 4 | Circle:7, Line:32
DISC-DISC-DISC_Fuse-TB_Round_R | DISC | 4 | 4 | Circle:7, Line:32
DISC-DISC-DISC_Fuse-TB_Square_L | DISC | 4 | 4 | Circle:6, Line:32, Polyline:1
DISC-DISC-DISC_Fuse-TB_Square_R | DISC | 4 | 4 | Circle:6, Line:32, Polyline:1
DISC-DISC-DISC_Fuse_L | DISC | 3 | 3 | Circle:6, Line:32
DISC-DISC-DISC_Fuse_R | DISC | 3 | 3 | Circle:6, Line:32
DISC-DISC-DISC_L | DISC | 3 | 3 | Circle:6, Line:11
DISC-DISC-DISC_R | DISC | 3 | 3 | Circle:6, Line:11
DISC-DISC-TB_Round_L | DISC | 3 | 3 | Circle:5, Line:7
DISC-DISC-TB_Round_R | DISC | 3 | 3 | Circle:5, Line:7
DISC-DISC-TB_Square_L | DISC | 3 | 3 | Circle:4, Line:7, Polyline:1
DISC-DISC-TB_Square_R | DISC | 3 | 3 | Circle:4, Line:7, Polyline:1
DISC-DISC_Fuse-TB_Round_L | DISC | 3 | 3 | Circle:5, Line:21
DISC-DISC_Fuse-TB_Round_R | DISC | 3 | 3 | Circle:5, Line:21
DISC-DISC_Fuse-TB_Square_L | DISC | 3 | 3 | Circle:4, Line:21, Polyline:1
DISC-DISC_Fuse-TB_Square_R | DISC | 3 | 3 | Circle:4, Line:21, Polyline:1
DISC-DISC_Fuse_L | DISC | 2 | 2 | Circle:4, Line:21
DISC-DISC_Fuse_R | DISC | 2 | 2 | Circle:4, Line:21
DISC-DISC_L | DISC | 2 | 2 | Circle:4, Line:7
DISC-DISC_R | DISC | 2 | 2 | Circle:4, Line:7
DISC-TB_Square_L | DISC | 2 | 2 | Circle:2, Line:4, Polyline:1
DISC-TB_Square_R | DISC | 2 | 2 | Circle:2, Line:10, Polyline:1
DISC_Fuse-TB_Round_L | DISC | 2 | 2 | Circle:3, Line:10
DISC_Fuse-TB_Round_R | DISC | 2 | 2 | Circle:3, Line:10
DISC_Fuse-TB_Square_L |  | 0 | 0 | BlockReference:2
DISC_Fuse-TB_Square_R |  | 0 | 0 | BlockReference:2
DISC_Fuse_L | DISC | 1 | 1 | Circle:2, Line:10
DISC_Fuse_R | DISC | 1 | 1 | Circle:2, Line:10
DISC_L | DISC | 1 | 1 | Circle:2, Line:4
DISC_R | DISC | 1 | 1 | Circle:2, Line:3
FlowSwitch_NC_L | FLS | 2 | 1 | Circle:2, Line:7
FlowSwitch_NC_R | FLS | 2 | 1 | Circle:2, Line:7
FlowSwitch_NO_L | FLS | 2 | 1 | Circle:2, Line:7
FlowSwitch_NO_R | FLS | 2 | 1 | Circle:2, Line:7
Fuse-TB_Round_L | FU | 2 | 2 | Circle:1, Line:6
Fuse-TB_Round_R | FU | 2 | 2 | Circle:1, Line:6
Fuse-TB_Square-Shld_L | FU | 3 | 3 | Arc:2, Line:12, Polyline:2
Fuse-TB_Square-Shld_R | FU | 3 | 3 | Arc:2, Line:12, Polyline:2
Fuse-TB_Square_L | FU | 2 | 2 | Line:6, Polyline:1
Fuse-TB_Square_R | FU | 2 | 2 | Line:6, Polyline:1
Fuse_L | FU | 1 | 1 | Line:6
Fuse_R | FU | 1 | 1 | Line:6
GND_L | GND | 1 | 1 | Circle:1
GND_R | GND | 1 | 1 | Circle:1
HOASwitch_NC_L |  | 1 | 1 | Circle:2, Line:3
HOASwitch_NC_R |  | 1 | 1 | Circle:2, Line:3
HOASwitch_NO_L |  | 1 | 1 | Circle:2, Line:3
HOASwitch_NO_R |  | 1 | 1 | Circle:2, Line:3
HTR_L | HTR | 2 | 1 | Circle:2, Line:16
HTR_R | HTR | 2 | 1 | Circle:2, Line:16
Inst_Pwr_Wire_L |  | 0 | 0 | Line:4
Inst_Pwr_Wire_R |  | 0 | 0 | Line:4
LC_L | LC | 1 | 1 | Line:19, Polyline:1
LC_R | LC | 1 | 1 | Line:19, Polyline:1
LevelSwitch_NC_L | FS | 2 | 1 | Circle:3, Line:5
LevelSwitch_NC_R | FS | 2 | 1 | Circle:3, Line:5
LevelSwitch_NO_L | FS | 2 | 1 | Circle:3, Line:5
LevelSwitch_NO_R | FS | 2 | 1 | Circle:3, Line:5
LightHorn_L | LT | 4 | 2 | Circle:1, Line:21
LightHorn_R | LT | 4 | 2 | Circle:1, Line:20
LimitSwitch_NC_L | LS | 2 | 1 | Circle:2, Line:6
LimitSwitch_NC_R | LS | 2 | 1 | Circle:2, Line:6
LimitSwitch_NO_L | LS | 2 | 1 | Circle:2, Line:6
LimitSwitch_NO_R | LS | 2 | 1 | Circle:2, Line:6
MTP_L | MTP | 1 | 1 | Circle:2, Line:27
MTP_R | MTP | 1 | 1 | Circle:2, Line:27
MTRStrt_L | M2 | 3 | 1 | Arc:6, BlockReference:1, Circle:6, Line:17
MTRStrt_R | M2 | 3 | 1 | Arc:6, Circle:6, Line:17
MTR_1PH_L | MTR | 3 | 1 | Circle:1, Line:6
MTR_1PH_NoGND_L | MTR | 2 | 1 | Circle:1, Line:4
MTR_1PH_NoGND_R | MTR | 2 | 1 | Circle:1, Line:5
MTR_1PH_R | MTR | 3 | 1 | Circle:1, Line:7
MTR_3PH_L | MTR | 4 | 1 | Circle:1, Line:7
MTR_3PH_NoGND_L | MTR | 3 | 1 | Circle:1, Line:5
MTR_3PH_NoGND_R | MTR | 3 | 1 | Circle:1, Line:6
MTR_3PH_R | MTR | 4 | 1 | Circle:1, Line:8
PressureSwitch_NC_L | PS | 2 | 1 | Arc:1, Circle:2, Line:6
PressureSwitch_NC_R | PS | 2 | 1 | Arc:1, Circle:2, Line:6
PressureSwitch_NO_L | PS | 2 | 1 | Arc:1, Circle:2, Line:6
PressureSwitch_NO_R | PS | 2 | 1 | Arc:1, Circle:2, Line:6
PullBox_L |  | 1 | 1 | Polyline:2
PullBox_R |  | 1 | 1 | Polyline:2
Pullrope_L |  | 0 | 0 | Polyline:1
Pullrope_R |  | 0 | 0 | Polyline:1
PushButton_NC_L |  | 2 | 1 | Circle:2, Line:5
PushButton_NC_R |  | 2 | 1 | Circle:2, Line:5
PushButton_NO_L |  | 2 | 1 | Circle:2, Line:5
PushButton_NO_R |  | 2 | 1 | Circle:2, Line:5
RECP_Duplex_L | RECP | 3 | 1 | Arc:1, Circle:1, Line:8
RECP_Duplex_R | RECP | 3 | 1 | Arc:1, Circle:1, Line:8
RECP_Simplex_L | RECP | 3 | 1 | Arc:1, Circle:1, Line:7
RECP_Simplex_R | RECP | 3 | 1 | Arc:1, Circle:1, Line:7
RJ45_L | RJ45 | 1 | 1 | Polyline:1
RJ45_R | RJ45 | 1 | 1 | Polyline:1
SC_L | SC | 1 | 1 | Circle:2, Line:13, Polyline:1
SC_R | SC | 1 | 1 | Circle:2, Line:13, Polyline:1
ST_L | ST | 1 | 1 | Arc:2, Circle:2, Line:8
ST_R | ST | 1 | 1 | Arc:2, Circle:2, Line:8
Shld-TB-TB-TB_Square_L |  | 4 | 4 | Arc:2, Line:6, Polyline:4
Shld-TB-TB-TB_Square_R |  | 4 | 4 | Arc:2, Line:6, Polyline:4
Shld-TB-TB_Square_L |  | 3 | 3 | Arc:2, Line:6, Polyline:3
Shld-TB-TB_Square_R |  | 3 | 3 | Arc:2, Line:6, Polyline:3
Spare_L |  | 1 | 0 | Arc:1, Text:1
Spare_R |  | 1 | 0 | Arc:1, Text:1
TB-SHLD-TB_Square_L |  | 2 | 2 | Arc:2, Line:6, Polyline:2
TB-SHLD-TB_Square_R |  | 2 | 2 | Arc:2, Line:6, Polyline:2
TB-TB-TB-TB_Round_L |  | 4 | 4 | Circle:4
TB-TB-TB-TB_Round_R |  | 4 | 4 | Circle:4
TB-TB-TB-TB_Square_L |  | 4 | 4 | Polyline:4
TB-TB-TB-TB_Square_R |  | 4 | 4 | Polyline:4
TB-TB-TB_Round_L |  | 3 | 3 | Circle:3
TB-TB-TB_Round_R |  | 3 | 3 | Circle:3
TB-TB-TB_Square-Shld_L |  | 4 | 4 | Arc:2, Line:6, Polyline:4
TB-TB-TB_Square-Shld_R |  | 4 | 4 | Arc:2, Line:6, Polyline:4
TB-TB-TB_Square-TB_Round_L |  | 4 | 4 | Circle:1, Polyline:3
TB-TB-TB_Square-TB_Round_R |  | 4 | 4 | Circle:1, Polyline:3
TB-TB-TB_Square_L |  | 3 | 3 | Polyline:3
TB-TB-TB_Square_R |  | 3 | 3 | Polyline:3
TB-TB_L |  | 2 | 2 | Polyline:2
TB-TB_Round_L |  | 2 | 2 | Circle:2
TB-TB_Round_R |  | 2 | 2 | Circle:2
TB-TB_Square-Shld_L |  | 3 | 3 | Arc:2, Line:6, Polyline:3
TB-TB_Square-Shld_R |  | 3 | 3 | Arc:2, Line:6, Polyline:3
TB-TB_Square-TB_Round_L |  | 3 | 3 | Circle:1, Polyline:2
TB-TB_Square-TB_Round_R |  | 3 | 3 | Circle:1, Polyline:2
TB-TB_Square_L |  | 2 | 2 | Polyline:2
TB-TB_Square_R | TB | 2 | 2 | BlockReference:1, Polyline:2
TB_Round_L |  | 1 | 1 | Circle:1
TB_Round_R |  | 1 | 1 | Circle:1
TB_Square-TB_Round_L |  | 2 | 2 | Circle:1, Polyline:1
TB_Square-TB_Round_R |  | 2 | 2 | BlockReference:1, Circle:1, Polyline:1
TB_Square_L |  | 1 | 1 | Polyline:1
TB_Square_R |  | 1 | 1 | Polyline:1
TemperatureSwitch_NC_L | TAS | 2 | 1 | Circle:2, Line:12
TemperatureSwitch_NC_R | TAS | 2 | 1 | Circle:2, Line:11
TemperatureSwitch_NO_L | TAS | 2 | 1 | Circle:2, Line:11
TemperatureSwitch_NO_R | TAS | 2 | 1 | Circle:2, Line:11
VFD_L | VFD | 3 | 1 | Arc:6, BlockReference:1, Circle:6, Line:17
VFD_R | VFD | 3 | 1 | Arc:6, Circle:6, Line:17
Valve_L | VALVE | 2 | 1 | Circle:2, Line:8
Valve_R | VALVE | 2 | 1 | Circle:2, Line:8
XFMR_1PH_L | XFMR | 2 | 1 | Arc:8, Circle:4, Line:16
XFMR_1PH_R | XFMR | 2 | 1 | Arc:8, Circle:4, Line:16
XFMR_3PH_L | XFMR | 3 | 1 | Arc:24, Line:14
XFMR_3PH_R | XFMR | 3 | 1 | Arc:24, Line:14